LOS ANGELES COUNTY FIRE – RESPONSE LETTER

Project Name: The Now (West Hollywood)

Job Address: 8497-8499 Sunset Blvd | West Hollywood, CA 90069

Permit #: TBD

Date: May 17, 2023

In regards to plan check comments:

* Building usage added to SITE INFORMATION section. [T-1.0]
* Architectural rendering added. [A-11.0 (3)]
* Applicable code years updated. [T-1.0]
* Donor antenna models and gain values updated. [GN-2]
* Density note added to all ERRCS | GENERAL NOTES. [A sheets]
* EMT note added to all ERRCS | CABLE NOTES. [A sheets]
* All components are already shown as 18” above the floor, which is more than 12 inches above the floor. Layout for headend equipment remains the same.
  + Mounting distance note added to ERRCS | EQUIPMENT ROOM NOTES. [A-10.0 (1)]
* Donor antennas updated. [EQ-1.0 (1)] [EQ-1.0 (2)]
* Ethernet switch and ethernet port added to CDs.
  + Headend room enlargement. [A-10.0 (1)]
  + Points of Alarming wiring diagram. [D-3.0(4)]
* Donor antenna mounting specifics added. [G-1.0(4)]

All corrections will be clouded and identified with a delta 0.